## Fire Door checks
Fire Door Inspection
Carried out by: | [6 empty] | Date:
No | Location | Intumescent Seals? | Labelled? | Good Condition? | Glazing & Glass | 3mm gap? | 3 hinges? | Door closures work? | Comments | Action Req Y/N
Inspection Guidance
Intumescent Seals
Are Intumescent seals in place?
Are the seals well attached inside the groove in the frame or door leaf?
Are the seals free from damage and paint?
If you have a brush or fin type seal, is it free from damage or breakage?
If fitted, are the smoke and acoustic seals continuous around the frame or door leaf?
Certification
Has the fire door got a certified Fire door scheme label on the top edge?
If not, can you confirm that the door is in fact a fire door and has been certificated as such?
Good Condition
Door Leaf
Does the leaf sit against the door stop and is free of distortion?
If the door is veneered or lipped, is the glue still holding these products firmly in place?
Is the door free from damage including dents, and holes?
Door Frame
Is the door frame firmly attached to the wall?
If a planted door stop is present, is it firmly attached?
Is the door leaf gap consistently 3mm?
Glazing and Glass
Is the Intumescent seal continuous and attached to the glass and bead?
Are the glazing beads well attached to the frame and free from damage?
Is the glass free from damage and cracking?
If the glass has been replaced, is it fire rated glass?
If glazing panels are below 1500mm from the bottom of the door, is the glass safety glass?
Threshold Gap
Is there a consistent gap under the door that allows it to swing without touching the floor covering?
Is the door to floor covering gap consistently 10mm (3mm if smoke seals are fitted) or less when the door is closed?
If the door leaf is fitted with a threshold seal, does the seal make contact with the floor covering when the door is closed?
Hinges
Is there a minimum of 3 hinges with all the screws fitted?
Are all the screws the correct size?
Are the hinges free of metal fragments and oil leakage? (These are signs of wear)
Are the hinges free from non-combustible packing?
Door Closers
Open the door to 5 degrees or 75mm. Does it close and engage with the latch?
Is the closer securely attached to the door and frame?
Is the closer free from damage and not leaking?
If unlatched, does the closer hold the door in line with the frame and Intumescent seal?
If hung in pairs, do they close in line if both opened and released together?
If hold open device is used, is it electronically released?
Does the hold open device release the door when required?

## Certification
Certification
• Just like any passive or active fire protection system, it is essential for a fire door to perform its vital task in the event of a fire.
• To satisfy UK Building Regulations, a door design must pass a recognised fire test, or an assessment based on test evidence. Tests are usually conducted in a United Kingdom Accreditation Service (UKAS) approved laboratory, with the intention of checking that the design meets current standards and to prove that it will hold back a fire for a prescribed period of time.
• The test is conducted on a door assembly which has been supplied by the manufacturer, with no independent selection or assurance that subsequent production will be to the same quality or specification.
• It is important to understand that a test report is only valid for the door assembly that has been tested. So a single leaf door assembly test is not valid for an assembly involving pairs of doors, nor a double acting single leaf door.
• The BWF recommends that all fire door designs should also be third party certificated to offer a safeguard for important aspects which are not covered in a single fire test.
• Third party certification tests and verifies a fire door’s design, performance, manufacturing process & the associated procedures, quality assurance, the audit trail from manufacture to installation and identification marking.
• Every fire door design manufactured under the BWF-CERTIFIRE Fire Door & Doorset Scheme has been independently tested and certificated as proof that, all things being equal, it will be reliable in the event of a fire. But it is not only the fire door itself that has to be certificated. Anyone involved in the handling of certificated doors, whether manufacturing the frames, inserting glass vision panels or installation, should be able to demonstrate through independent certification that they are capable of doing the job to the required standard.
• Although it is vital to use certificated components when completing a fire door assembly, it is also important to ensure that the components used are compatible. It is wrong to assume that all certificated components will work effectively together.
Proper installation is integral to fire door performance. It is one of the final and, arguably, most crucial stages of the work carried out on fire doorsets. As manufacturers & suppliers go through the extensive and committed process of having their doors and components rigorously tested in accordance to the latest standards, the installation procedures become ever more important to ensure that the fire door remains fully reliable.
The correct installation of fire door assemblies and doorsets is fundamental to their overall performance because it will ensure the fire door will remain reliable to its fire integrity rating in the event of a fire.
A fire doorset is correctly installed in the furnace when it is tested, so therefore it must be installed correctly on site so that the door will perform in the same way when needed.
Incorrect installation defeats the purpose of certificated fire doors, certificated components and certificated hardware because in a fire, the smoke and gases it produces can easily travel through the gaps left by incorrect installation.
A certificated half hour fire door which is incorrectly installed may only provide 5-10 minutes of fire resistance.
In order to avoid risking people’s lives, BWF-CERTIFIRE manufacturers (who account for 90% of all fire doors manufactured in the UK) provide specific and comprehensive installation instructions with every door which must be rigorously followed by the installer.
Installation instructions are specifically written for each particular door design in accordance with its relevant fire test. THEREFORE, INSTALLING FIRE DOORS IS NOT A STANDARD TASK, IT IS A SPECIALISED TASK.
The advice in the installation instructions just takes a moment to read and even though installers may have been fitting fire doors for years, the instructions will inform the reader of detail specific to that door. More importantly, it will offer that peace of mind to the installers and will result in fewer site difficulties.
As fire door designs are constantly changing, correct installation has become ever more vital. Not following the instructions can prove fatal in the event of a fire and will invalidate the certification because installation is the last stage of the entire certification process.
If you come across a BWF-CERTIFIRE certificated fire door that – for whatever reason – does not have these installation instructions, then you should speak to the site manager from where you obtained the door or contact the manufacturer of the fire door; details can be found on the label stuck on top of the fire door leaf.
If there are no instructions, you may be installing a fire door that has not been third party certificated. The BWF recommends that you contact the manufacturer of that fire door and obtain instructions direct from them.
Ideally, a non-certificated fire door should not be installed where a fire door is necessary and it is highly recommended that you change your supplier in order to obtain fire doors manufactured under the BWF-CERTIFIRE Fire Door & Doorset Scheme.
The BWF is committed to supporting FIRAS, the third party certification Scheme for the installation of passive fire protection products. Members are trained and taught how exactly to install a fire door. All certificated FIRAS Installers are obliged to stick a unique and fully traceable label on every fire door they install (this is also an excellent source of marketing for the installer).

## Seals
Seals
Fire doors play a crucial role in restricting the spread of fire and smoke. If a door is to work effectively in its normal role the door leaf must be free to move within the frame, and in order to achieve this there must be a gap around the perimeter. If the gap is too wide, it may compromise the door’s ability to restrict the spread of fire and smoke. Intumescent materials and smoke seals play a major role in restricting fire and smoke spread, and hence reducing incidences of death and injury and reducing property damage.
When do you use fire seals?
The Building Regulations indicate where you need fire doors and that these would need intumescent seals. But they also indicate those situations where a fire door may also have to prevent smoke leakage, and in those situations a smoke seal must be fitted. You can buy intumescent seals that combine a smoke seal or you can fit two separate seals - a fire seal and a separate smoke seal. Fire doors are designated by their required period of fire resistance; FD30, FD60, FD90 and FD120.
The Door Gap
The gap between the door leaf and the frame must be suitable for the intumescent seal fitted. In general, the gap should not exceed 3mm. To facilitate the checking of this gap on site, the BWF-CERTIFIRE Fire Door & Doorset Scheme has produced a gap tester which can be used for this purpose. The bwfgaptester is available free of charge from the BWF.
Intumescent Fire Seals and Glazing Systems
Intumescent fire resistant seals are also used as part of a glazing system which secures and seals the glass in fire door vision panels. Fire seals contain intumescent material. This material expands when exposed to heat. When a fire door is exposed to a fire, these seals heat up and expand to many times their original size, sealing the gap between the door and the doorframe to stop the fire spreading. Intumescent fire seals are normally fitted into a groove on the doorframe, although they can be fitted into the edge of the door leaf and are unobtrusive in the day-to-day use of the door. Properly specified and installed, these seals will lie dormant for years, only activating when subjected to the high temperature and pressure conditions of a fire.
Spreading smoke is a major cause of death and injury in fires, as well as a large contributor to the cost of fire damage, therefore the containment of smoke is vital. Many of the fire resisting door assemblies used in buildings are also required to provide a smoke control function. Fire doors, which also require smoke protection, are designated FD30S, FD60S, FD90S and FD120S. Smoke seals control the leakage of air and smoke through vulnerable parts of the door, around the perimeter and when required at the threshold. Types of Smoke Seals: There are two main types of edge seals capable of providing the specified smoke leakage rates; 1. Deflection or Compression seals, normally fitted to the doorstop to produce contact with the face of the door. 2. Wiping seals fitted in the leaf edge or in the frame opposite the edge, or at the threshold at the bottom of the door.
Combined Fire and Smoke Seals
Combined seals incorporate intumescent material with a smoke seal and allow for one product to be fitted to perform both fire and smoke protection functions. When specifying any component for a fire door, including fire seals, it is imperative to follow the manufacturer’s instructions and specifications for the particular door design. For a single leaf, single acting FD30 door, it may be possible to interchange intumescent seals with a CERTIFIRE approved seal. However for FD60 and above, the installer must comply with the door manufacturer’s tested and recommended solution. If seals are required for fire and smoke doors then the seals must not only be CERTIFIRE approved for fire but additionally for smoke. If fire and smoke seals are not factory fitted, it is essential to consult the fire door manufacturer to determine exactly which seal specification has been tested for the particular door assembly.
During the development of the BWF-CERTIFIRE Fire Door & Doorset Scheme the BWF Manufacturers decided that, to ensure the integrity of the fire door assembly, all scheme fire door assemblies should be fitted with intumescent seals. The companies in the BWF-CERTIFIRE Fire Door & Doorset Scheme, including the suppliers of seals, have all tested their products in a UKAS accredited (United Kingdom Accreditation Service) facility and have demonstrated that they meet the requirements of the Building Regulations. These companies also voluntarily undergo independent audits to verify the continuing quality and fitness for purpose of their products. The manufacturer’s Installation instructions can be found on the fire door or on individual company websites. The BWF-CERTIFIRE Fire Door & Doorset Scheme directory lists all the scheme’s current members and can be obtained via the BWF or the BWF website. Seals that carry the relevant CERTIFIRE approval must be fitted to doors, frames or doorsets supplied by door manufacturer members of the BWF-CERTIFIRE Fire Door & Doorset Scheme.
* CERTIFIRE is the independent third party certification body which carries out type and audit testing of all products within the BWF-CERTIFIRE Fire Door & Doorset Scheme for fire performance, together with factory production control. This ensures that the products supplied and installed provide the same level of performance as those tested.

## Glass & Glazing
Glass & Glazing
Many timber doors include glazed apertures, either as a design feature or in order to comply with Building Regulations.
However, when the door is a fire door, all the elements of the glazed aperture must, when used together, be capable of withstanding the fire. They must not reduce the overall effectiveness of the door in holding back a fire.
This fact card is intended to provide some basic essential information on the correct way to specify and use glazed apertures in 30-minute fire doors (FD 30). It tells you what to look for and how to ensure that you are using the correct life-protecting materials.
Most fire doors manufactured in the UK are manufactured as fire door leaves. Before they are installed, many will be modified in some way, whether by the addition of a door frame, the insertion of a glazed aperture or other types of apertures, or, ideally, conversion into a complete fire doorset or assembly.
Glazed apertures provide added safety in everyday use. In the event of a fire, they aid detection of fire and smoke, whilst providing visibility to potential escape routes.
The size and positioning of apertures is very important, as this will ultimately have a bearing upon the behaviour of the fire door assembly in the event of a fire.
Cutting apertures for glazing and other apertures in a fire door on site IS NOT permitted (even by an approved aperture cutter), under the BWF-CERTIFIRE Fire Door and Doorset Scheme.
Glazing pre-cut apertures in fire doors on site is permitted, but MUST be undertaken by a trained and competent installer in accordance with the instructions provided by the door manufacturer.
The BWF recommends that fire doors should only be glazed by certificated members of the BWF-CERTIFIRE Scheme or by FIRAS registered installers in order to maintain the door’s full certification.
Key Elements (see also section detail)
The following elements are essential for the success of any properly installed glazed aperture in a 30-minute (FD 30) fire door assembly.
Aperture – only certain door types are designed to perform with glazed apertures. Make sure that any aperture has been properly formed, either by the original door manufacturer, or by one of his approved “aperture formers”. If the aperture is cut in an unsuitable door type, or by someone who does not recognise the correct procedure and materials, the whole fire resistant property of the door leaf may be destroyed.
Depending on the door’s construction, an aperture liner of wood or intumescent material may be needed. If a door is suitable for glazed apertures, the door manufacturer should indicate the relevant:
| • Aperture size | • Type of apertures
| • No of apertures | • Glazing systems
• Location of apertures
In every case, the door manufacturer must be able to supply evidence that he holds test certification for the specific door design. If this cannot be provided, there is no proof that the installation would work in a fire, and the inspecting authority may refuse to accept it.
Glass – a specialist fire glass must be used. There are four quite separate types of fire glass, each of which performs in its own individual way. Never assume that a system which has been tested or certificated for one specific glass may be suitable for a different glass, unless the manufacturer can provide his own test evidence or certification.
The fire glass types are:
| • Imbedded wired glass |  | • Special glass composition (this needs precisely detailed edge cover and clearances) – borosilicate, ceramic etc.
| • Specially tempered/toughened glass |  | • Laminated glass with reactive fire resisting interlayer(s)
The door manufacturer should specify:
| • Type of glass |  | • Special glazing requirements, especially edge
| • Thickness cover/clearances, setting block types |  | • Aspect ratio
| • Suitability for door type |  | • Maximum dimensions of glass
As with apertures, the door manufacturer must be able to supply test evidence to support the specification.
Beads and Fixings – the beads and their fixing are absolutely vital in retaining the fire glass in place for the whole of the required time period.
Attention must be paid especially to:
• Bead material: If timber beads are used, it is particularly important to use the current species
• Bead size and shape: There must be enough material to char throughout the whole fire test (although angled beads are shown in the diagram, some glass types will permit the use of flat timber beads)
• Frequency, size and type of bead fixings: screws, pins or brads
• Angle of fixing: see diagram
• Glass edge cover and clearances
Glazing seals – Whatever glazing medium is used, it must hold test certification for the particular panel size and application within the door design and be appropriate and compatible with the chosen glass type.
The seals between the glass and beads on each side may take the form of:
• Pre-formed rigid or flexible strips
• Pre-formed channels to wrap around the edge of the glass
• Gun-able mastic compounds
The BWF-CERTIFIRE Fire Door & Doorset Scheme Directory provides a complete list of fully certificated manufacturers and suppliers. Details can be found on the BWF website at www.bwf.org.uk
For more detailed information on a specific door or glazing, please contact the door manufacturer or glass manufacturer, who will hold full details of test certification.
The use of vision panels in 60-minute timber fire doors (FD 60) is a completely separate (and much more complex) subject. It requires different glass types, glazing methods and bead sizes. Contact the door manufacturers or glass manufacturers who offer FD 60 products for specific details.
More detailed information about fire-resistant glazing can be found in the “Fire Glazing – Best Practice Guide” produced by the Glass and Glazing Federation. Contact the GGF at www.ggf.org.uk

## Hinges
Hinges
Ironmongery on fire doors
Just like any passive or active fire protection system, it is essential for a fire door to perform its vital task in the event of a fire.
A fire door is not just the door leaf. It consists of the frame, any glazing, the intumescent fire and smoke seals and all the ironmongery.
Ironmongery includes all the items that are used on a fire door, such as the hinges, overhead door closers, latches, locks and handles.
These components are crucial when making up a fire doorset.
The fire door will not work in the event of a fire unless all the correct ironmongery has been fitted and maintained!
All ironmongery needs to be certificated and compatible with the fire door. If not, then the fire door will not provide its true performance level.
Selection of Ironmongery
Every fire door designed and manufactured under the BWF-CERTIFIRE Fire Door & Doorset Scheme has been independently tested and certificated to prove that, all things being equal, it operates reliably in normal use and in the event of a fire.
Fire doors can only be tested as complete assemblies. The specific ironmongery may only be reliable and compatible with the particular fire door assembly with which it has been tested.
All certificated ironmongery products are then issued with a certificate number.
Fire door leaves and ironmongery are often sold separately.
They are then bought separately – THIS IS WHERE THE DANGER LIES !!
It is absolutely crucial that when selecting ironmongery that only certificated and compatible ironmongery is selected.
Maintenance of ironmongery
All ironmongery needs to be regularly checked.
Check that there is no visible wear on the hinge. Any dark marks or stains around the hinge knuckle could indicate wear and impending failure, meaning that the hinges should be replaced as soon as possible. (Figure 1)
Check that the door closing device is operating correctly. Ensure that the doors are not being wedged open. Open the door fully and check it closes without binding on the floor. Open the door to approximately 5 degrees and again check that it closes fully, overcoming any latch or seal. Check door closing speed to be approximately 10 seconds from 90 degrees and ensure that the door does not slam. Adjust speeds as necessary.
Make sure that any electro-magnetic hold-open device is operating correctly and releases immediately when power is removed.
Check that the levers fully return to the horizontal after use and that the latchbolt is engaging smoothly and completely into the strike. Wipe any metal dust deposits off the latchbolt and strikeplate. Adjust, lubricate or replace, as required. (Figure 2)
Make sure that all fixings are secure. Some hinges, closer arms and locks may require lubrication. (See manufacturers’ installation instructions).
CE marking of ironmongery (Figure 3)
CE Marking is required under the Construction Products Directive (CPD) to confirm that construction products, which are placed on the market within Europe, meet the Essential Requirements set out in the CPD:
• Mechanical Stability
• Fire Safety
• Health & Environmental Safety
• Sound Protection
• Energy Efficiency
CE Marking allows a simple route to satisfying the Construction Products Regulations which apply the Directive and its requirements in the UK.
CE Marked hinges, tested to BS EN1935, should be used on fire or smoke doors and on all routes of escape.
CE Marking of door closing devices, electro-magnetic closing devices and door co-ordinators tested to BS EN1154/55/58 will be required towards the end of 2004.
BWF-CERTIFIRE Fire Door & Doorset Scheme
• All ironmongery manufacturers within the BWF-CERTIFIRE Fire Door & Doorset Scheme have had their relevant product ranges tested.
• This is the first step to ensuring you use the correct compatible ironmongery for the fire door design – you must ensure that the ironmongery is certificated.
• Always ensure that you fit the correct compatible components as per the fire door manufacturer’s installation instructions.
• Ensure the ironmongery is maintained regularly in accordance with the ironmongery manufacturer’s recommendations.
Details of compatible components are available from the BWF and are explained in the manufacturers’ installation, care & maintenance instructions attached to every door manufactured by Members of the BWF-CERTIFIRE Fire Door & Doorset Scheme.

## Frames
Frames
The old custom and practice of ‘knocking up’ fire door frames, hanging a fire door leaf and believing that the results constituted a valid fire door installation was never correct, undoubtedly placing property and lives at risk. The best way to ensure that a fire door is installed using the correct frame is by purchasing a fire door frame from the door leaf manufacturer, preferably as part of a door set, or from a company certificated to produce fire door frames for that manufacturer’s door. This ensures that you get a fully compatible and certificated end product.
What is the difference between a fire door frame, fire door lining and fire door casing?
Door Frame: A component delivered pre-assembled into which a door leaf can be hung. A frame is usually rebated to create the door stop.
Door Lining: A kit of components usually consisting of two stiles and a head which when assembled on site can accept a door leaf. Once a door leaf is fitted, door stops will need to be added.
Door Casing: Similar to a door lining, except that the door stops are created by pre-rebating the components.
All should be grooved to take an intumescent seal.
Ensuring the Correct Specification:
It is very important to specify all fire door components correctly. A fire door is more than just a door leaf. The door frame, hinges, ironmongery, seals and the glass in vision panels must all be selected, from installation instructions, to ensure that the door assembly design is properly fire resistant and that all the components work when used in combination.
Specifying Fire Door Frames
30 minute fire door frames can be made from softwood or hardwood with a minimum density of 510kg/m3. 60 minute fire door frames should always be made from hardwood with a minimum density of 650kg/m3. Densities less than this are acceptable if stated in the door leaf manufacturer’s installation instructions.
To ensure the proposed species of timber used in a door frame is compatible with the tested design, you should check the suitability of different species with the fire door manufacturer. MDF is now also widely used for 30 minute fire door frames; however, it is important to check the installation instructions, as MDF cannot be used with all manufacturers’ doors.
Minimum dimensions will be dictated by the fire test report, but as a general principle, the frame must be thick enough to take the full length of the screw used. Although frames of 30mm thickness are preferred, they may vary according to installation instructions. It is generally accepted that intumescent seals should be used with all fire doors. Their use ensures that the selection of door stops is no longer critical from a fire performance perspective. Stops of 12mm are typical, but may vary according to installation instructions.
Unless the intumescent seal is located in the door edge, it should be fitted into the frame. To facilitate fitting, the frame should be grooved to the size of the seal specified. Generally a 15mm x 4mm seal will be acceptable for a 30 minute fire door. 60 minute doors require a higher seal specification, which may involve using two seals fitted in tandem. It is important to check the correct seal specifications on the door’s installation instructions. If smoke seals are required, separate or combined seals may be used.
The internal dimensions of a frame should be such that the gap left between the frame and the door leaf, when fitted, meets the requirements of the fire installation instructions. Generally, this gap is 3mm, but where smoke seals are used, it may be necessary to increase the gap to facilitate the operation of the doors.
Installing a Fire Door Frame:
Installations should only be carried out by competent professionals. Please contact the BWF or visit www.warringtonfire.net for a full list of approved installers.
Under the BWF-CERTIFIRE Scheme, all fire doors and doorsets are supplied with specific and comprehensive installation instructions from their manufacturers. These must be followed exactly if certification is to remain valid.
The frame must be fixed securely to the surrounds, with gaps generally not exceeding 10mm between the frame and the wall, which must be filled with suitable material such as intumescent mastic or mineral fibre. The frame can be rebated to create a stop or the stop may be planted and either pinned or pinned and glued.
Re-using Existing Frames
There may be circumstances where fitting new frames is not possible or practicable. If existing frames are to be re-used, a number of additional steps may be necessary:
1. Grooving an existing frame to take an intumescent seal is possible, but can be difficult. Grooving the door leaf is an alternative option, although care must be taken to ensure that the fire door label is not damaged.
2. The architraves must be removed on at least the hanging side of the frame. This enables inspection of the joint between the frame and wall to ensure adequate sealing (just as for new frames, the gap between the frame and wall must be fully sealed).
3. The thickness of the frame should be checked to ensure it meets the requirements of the installation instructions, and guidance sought if undersize.
Fire doors which fail cost lives and property!
The BWF-CERTIFIRE Fire Door & Doorset Scheme has developed a specification for a standard fire door frame, which is compatible with a majority of FD30 fire doors manufactured under the scheme. All fire door frames manufactured to the standard frame specification and manufactured under the BWF-CERTIFIRE Fire Door & Doorset Scheme can be identified by the label (images 1–4) on each frame.
To find out which companies are licensed and certificated to manufacture compatible fire door frames, please refer to the Scheme Directory, the BWF website or contact the BWF.